# Design Basis and Requirements Specification

## Project Overview

The project consists of producing a conceptual 11kV electrical distribution network for a new multidisciplinary scientific research campus. The design represents a concept-stage engineering study and is not intended for construction.

## Client Requirements

Incoming supply: One 11 kV feeder

Distribution voltage: 11 kV

Utilisation voltage: 400/230 V

Design Objectives:

- Reliability

- Maintainability

- Safety

- Expandability

- Efficiency

## Site Information

The site is a multidisciplinary scientific research campus, consisting of 6 buildings: Administration, Laboratory A, Laboratory B, Cryogenic Plant, Data Centre and Workshop. The total size of the site is approximately 500 m x 350 m.

## Load Schedule

| Building | Peak Demand |
| --- | --- |
| Administration | 250 kW |
| Laboratory A | 900 kW |
| Laboratory B | 1.2 MW |
| Cryogenic Plant | 1.8 MW |
| Data Centre | 1.5 MW |
| Workshop | 600 kW |
| Future Expansion | 2 MW |

## Design Constraints

Diversity factor: 0.82

Power factor: 0.95 lagging

Maximum voltage drop: 5%

Ambient temperature: 30°C

## Applicable Standards

| Standard | Scope | Relevance |
| --- | --- | --- |
| BS EN 61936-1 | Power installations exceeding 1 kV AC. | Primary design standard for the 11 kV distribution network, substations, and equipment layout. |
| BS EN 50522 | Earthing of power installations exceeding 1 kV AC. | Provides guidance for the design of the HV earthing system and personnel safety. |
| BS 7671 | Requirements for Electrical Installations (IET Wiring Regulations). | Governs the 400/230 V low-voltage installations supplied from the transformers. |
| IEC 60909 | Short-circuit currents in three-phase AC systems. | Defines the methodology for calculating fault currents used in equipment selection and protection studies. |
| IEC 60287 | Calculation of current rating for power cables. | Used to determine cable current-carrying capacity during cable sizing. |
| IEC 60502-2 | Power cables with extruded insulation for rated voltages from 6 kV to 30 kV. | Provides requirements for the specification and selection of 11 kV power cables. |

## Assumptions Register

| ID | Assumption | Reason |
| --- | --- | --- |