# Conceptual Design of a Medium Voltage Electrical Distribution Network
for a Scientific Research Campus

Project Duration: 8–10 weeks
Objective: Develop a professional conceptual HV distribution design package demonstrating graduate-level engineering judgement, documentation, calculations and CAD skills.

## Background

A new multidisciplinary research campus is to be constructed. The campus contains laboratories, experimental facilities, offices and mechanical plant. The client requires a conceptual electrical design for the primary medium-voltage distribution network. This is a concept design rather than a construction-ready design.

## Software

• AutoCAD (Mac)

• Python

• Visual Studio Code

• Git/GitHub

• Excel (optional)

## Client Requirements

Incoming utility supply: One 11 kV feeder

Primary distribution: 11 kV

Utilisation voltage: 400/230 V

Objectives:

- High reliability

- Maintainability

- Safety

- Future expansion

- Efficient operation

## Site Data

Campus size: approximately 500 m × 350 m

Peak demands:

- Administration Building: 250 kW

- Laboratory A: 900 kW

- Laboratory B: 1.2 MW

- Cryogenic Plant: 1.8 MW

- Data Centre: 1.5 MW

- Workshop: 600 kW

- Future Expansion: 2.0 MW

Assume:

- Diversity factor: 0.82

- Power factor: 0.95 lagging

- Maximum voltage drop: 5%

- Ambient temperature: 30 °C

## Engineering Tasks

1. Produce a design requirements specification.

2. Calculate maximum demand and transformer requirements.

3. Compare radial, ring-main and double-ended network topologies before selecting one.

4. Produce professional single-line diagrams in AutoCAD.

5. Select transformers and justify ratings, redundancy and loading.

6. Size cables using current capacity, voltage drop and short-circuit withstand calculations.

7. Perform simplified three-phase and earth fault calculations.

8. Develop a protection philosophy covering overcurrent, earth fault and transformer protection.

9. Develop an earthing philosophy and discuss safety considerations.

10. Assess system reliability under transformer, feeder and breaker failures.

11. Estimate transformer and cable losses and discuss efficiency improvements.

12. Demonstrate how the network could be expanded in the future.

## Deliverables

• Engineering Design Report (~60 pages)

• AutoCAD single-line diagrams (PDF)

• Site layout drawing

• Python calculation package

• Engineering assumptions register

• Design risk register

• Professional GitHub repository with documentation

## Suggested Report Structure

1. Executive Summary

2. Introduction

3. Design Requirements

4. Engineering Assumptions

5. Load Assessment

6. Network Topology Selection

7. Transformer Selection

8. Cable Sizing

9. Voltage Drop Analysis

10. Fault Level Analysis

11. Protection Philosophy

12. Earthing Philosophy

13. Reliability Assessment

14. Energy Efficiency

15. Future Expansion

16. Conclusions

17. References

18. Appendices

## Stretch Goals

• Python cable sizing tool

• Fault current calculator

• Voltage drop calculator

• Automatic report generation

• Interactive command-line design tools

## Skills Demonstrated

• Power systems engineering

• HV distribution concepts

• Engineering calculations

• AutoCAD

• Python programming

• Technical report writing

• Systems engineering

• Engineering judgement

• Version control with Git

## Advice

Treat this project as if you are producing a consultancy concept design. Record assumptions, justify decisions, revise your design when calculations change, and document the reasoning behind every engineering choice.